## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'D': 75.0-150.0 ton, 4.88 COP, 6.28 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | a634760c-ef53-4c34-86cc-a5d0c2a633d7 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'D' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.016952 | 277.0389 | 0.022163 | 285.9278 | 1 | 18349.9844 | 100489.3949 | 118839.3792 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 285.9278 | 2 | 28212.3316 | 200978.7897 | 229191.1213 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 285.9278 | 3 | 42366.5815 | 301468.1846 | 343834.7661 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 285.9278 | 4 | 60812.7341 | 401957.5794 | 462770.3135 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 295.0019 | 1 | 20915.7238 | 95153.5109 | 116069.2347 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 295.0019 | 2 | 32157.0484 | 190307.0218 | 222464.0701 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 295.0019 | 3 | 48290.3799 | 285460.5326 | 333750.9125 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 295.0019 | 4 | 69315.7184 | 380614.0435 | 449929.7619 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 304.0759 | 1 | 23989.8077 | 87602.3892 | 111592.1969 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 304.0759 | 2 | 36883.3235 | 175204.7784 | 212088.1019 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 304.0759 | 3 | 55387.8479 | 262807.1676 | 318195.0155 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 304.0759 | 4 | 79503.3809 | 350409.5568 | 429912.9377 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 313.15 | 1 | 26831.758 | 77836.0298 | 104667.7879 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 313.15 | 2 | 41252.7029 | 155672.0597 | 196924.7626 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 313.15 | 3 | 61949.3641 | 233508.0895 | 295457.4535 | 0 | 0 | NORMAL
0.016952 | 277.0389 | 0.022163 | 313.15 | 4 | 88921.7414 | 311344.1193 | 400265.8607 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 285.9278 | 1 | 18717.4667 | 113195.1327 | 131912.5994 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 285.9278 | 2 | 28777.3203 | 226390.2653 | 255167.5856 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 285.9278 | 3 | 43215.0274 | 339585.398 | 382800.4254 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 285.9278 | 4 | 62030.5883 | 452780.5306 | 514811.1189 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 295.0019 | 1 | 21497.8871 | 107998.8645 | 129496.7516 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 295.0019 | 2 | 33052.1 | 215997.729 | 249049.829 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 295.0019 | 3 | 49634.4828 | 323996.5935 | 373631.0763 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 295.0019 | 4 | 71245.0356 | 431995.4579 | 503240.4935 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 304.0759 | 1 | 25105.7768 | 100587.3586 | 125693.1354 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 304.0759 | 2 | 38599.0792 | 201174.7173 | 239773.7964 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 304.0759 | 3 | 57964.4057 | 301762.0759 | 359726.4816 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 304.0759 | 4 | 83201.7563 | 402349.4345 | 485551.1908 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 313.15 | 1 | 28830.9907 | 90960.6151 | 119791.6058 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 313.15 | 2 | 44326.4394 | 181921.2302 | 226247.6695 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 313.15 | 3 | 66565.2074 | 272881.8452 | 339447.0527 | 0 | 0 | NORMAL
0.016952 | 280.9278 | 0.022163 | 313.15 | 4 | 95547.295 | 363842.4603 | 459389.7553 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 285.9278 | 1 | 18997.7325 | 119408.7348 | 138406.4673 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 285.9278 | 2 | 29208.2171 | 238817.4695 | 268025.6867 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 285.9278 | 3 | 43862.1072 | 358226.2043 | 402088.3115 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 285.9278 | 4 | 62959.4026 | 477634.9391 | 540594.3416 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 295.0019 | 1 | 21646.3803 | 114352.0824 | 135998.4628 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 295.0019 | 2 | 33280.4021 | 228704.1648 | 261984.567 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 295.0019 | 3 | 49977.3251 | 343056.2473 | 393033.5724 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 295.0019 | 4 | 71737.1494 | 457408.3297 | 529145.479 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 304.0759 | 1 | 25306.0231 | 107080.1924 | 132386.2155 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 304.0759 | 2 | 38906.9495 | 214160.3848 | 253067.3342 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 304.0759 | 3 | 58426.7358 | 321240.5772 | 379667.313 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 304.0759 | 4 | 83865.3822 | 428320.7695 | 512186.1517 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 313.15 | 1 | 29296.8486 | 97593.0647 | 126889.9132 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 313.15 | 2 | 45042.6763 | 195186.1293 | 240228.8056 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 313.15 | 3 | 67640.7835 | 292779.194 | 360419.9775 | 0 | 0 | NORMAL
0.016952 | 284.8167 | 0.022163 | 313.15 | 4 | 97091.1704 | 390372.2586 | 487463.429 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 285.9278 | 1 | 19517.5722 | 119130.2012 | 138647.7734 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 285.9278 | 2 | 30007.4489 | 238260.4024 | 268267.8513 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 285.9278 | 3 | 45062.317 | 357390.6036 | 402452.9206 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 285.9278 | 4 | 64682.1764 | 476520.8048 | 541202.9812 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 295.0019 | 1 | 21760.83 | 114213.1647 | 135973.9947 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 295.0019 | 2 | 33456.3638 | 228426.3294 | 261882.6931 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 295.0019 | 3 | 50241.5675 | 342639.494 | 392881.0615 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 295.0019 | 4 | 72116.4412 | 456852.6587 | 528969.0999 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 304.0759 | 1 | 25063.0091 | 107080.8905 | 132143.8996 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 304.0759 | 2 | 38533.3256 | 214161.7809 | 252695.1066 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 304.0759 | 3 | 57865.6633 | 321242.6714 | 379108.3347 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 304.0759 | 4 | 83060.0221 | 428323.5619 | 511383.584 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 313.15 | 1 | 28774.6301 | 97733.3786 | 126508.0087 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 313.15 | 2 | 44239.7873 | 195466.7571 | 239706.5444 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 313.15 | 3 | 66435.0816 | 293200.1357 | 359635.2173 | 0 | 0 | NORMAL
0.016952 | 288.7056 | 0.022163 | 313.15 | 4 | 95360.5132 | 390933.5142 | 486294.0274 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F2: Data group defining the lookup variables for cooling performance
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B2: Data group defining the lookup variables for standby performance
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.016952 | 277.0389 | 15000
0.016952 | 280.9278 | 15000
0.016952 | 284.8167 | 15000
0.016952 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.022163 | 285.9278 | 15000
0.022163 | 295.0019 | 15000
0.022163 | 304.0759 | 15000
0.022163 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on C3: Pressure difference across the condenser