## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'E': 150.0-300.0 ton, 5.33 COP, 6.51 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | c63103f5-2403-45ee-a02f-49c196578a16 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'E' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.033905 | 277.0389 | 0.043699 | 285.9278 | 1 | 34582.0899 | 191894.2227 | 226476.3126 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 285.9278 | 2 | 50636.0565 | 383788.4454 | 434424.5019 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 285.9278 | 3 | 74151.1579 | 575682.6681 | 649833.826 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 285.9278 | 4 | 105127.3942 | 767576.8908 | 872704.285 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 295.0019 | 1 | 42228.6485 | 190688.4739 | 232917.1224 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 295.0019 | 2 | 61832.3599 | 381376.9478 | 443209.3077 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 295.0019 | 3 | 90546.9621 | 572065.4217 | 662612.3837 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 295.0019 | 4 | 128372.4549 | 762753.8955 | 891126.3504 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 304.0759 | 1 | 49229.3718 | 182087.7404 | 231317.1122 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 304.0759 | 2 | 72083.0135 | 364175.4808 | 436258.4943 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 304.0759 | 3 | 105557.9618 | 546263.2212 | 651821.183 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 304.0759 | 4 | 149654.2167 | 728350.9616 | 878005.1784 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 313.15 | 1 | 54301.4101 | 166092.0223 | 220393.4324 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 313.15 | 2 | 79509.6329 | 332184.0446 | 411693.6774 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 313.15 | 3 | 116433.4617 | 498276.0669 | 614709.5286 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.043699 | 313.15 | 4 | 165072.8966 | 664368.0891 | 829440.9858 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 285.9278 | 1 | 34654.4846 | 207646.9903 | 242301.4749 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 285.9278 | 2 | 50742.0588 | 415293.9806 | 466036.0395 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 285.9278 | 3 | 74306.3872 | 622940.9709 | 697247.3581 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 285.9278 | 4 | 105347.4696 | 830587.9613 | 935935.4309 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 295.0019 | 1 | 42470.8468 | 207746.6494 | 250217.4962 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 295.0019 | 2 | 62186.9935 | 415493.2988 | 477680.2923 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 295.0019 | 3 | 91066.2855 | 623239.9482 | 714306.2337 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 295.0019 | 4 | 129108.7228 | 830986.5977 | 960095.3204 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 304.0759 | 1 | 50042.2846 | 200451.3239 | 250493.6084 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 304.0759 | 2 | 73273.3029 | 400902.6477 | 474175.9507 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 304.0759 | 3 | 107301.015 | 601353.9716 | 708654.9866 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 304.0759 | 4 | 152125.4208 | 801805.2955 | 953930.7163 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 313.15 | 1 | 56197.9467 | 185761.0137 | 241958.9604 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 313.15 | 2 | 82286.5944 | 371522.0273 | 453808.6218 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 313.15 | 3 | 120500.0287 | 557283.041 | 677783.0697 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.043699 | 313.15 | 4 | 170838.2495 | 743044.0547 | 913882.3041 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 285.9278 | 1 | 35023.5825 | 214532.1588 | 249555.7412 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 285.9278 | 2 | 51282.5022 | 429064.3175 | 480346.8197 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 285.9278 | 3 | 75097.8094 | 643596.4763 | 718694.2857 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 285.9278 | 4 | 106469.5041 | 858128.6351 | 964598.1392 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 295.0019 | 1 | 42562.3569 | 215937.2258 | 258499.5827 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 295.0019 | 2 | 62320.9851 | 431874.4516 | 494195.4367 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 295.0019 | 3 | 91262.5021 | 647811.6774 | 739074.1795 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 295.0019 | 4 | 129386.9078 | 863748.9032 | 993135.811 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 304.0759 | 1 | 50098.1919 | 209947.3082 | 260045.5 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 304.0759 | 2 | 73355.1639 | 419894.6164 | 493249.7803 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 304.0759 | 3 | 107420.8918 | 629841.9245 | 737262.8163 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 304.0759 | 4 | 152295.3755 | 839789.2327 | 992084.6082 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 313.15 | 1 | 56572.2348 | 196562.4059 | 253134.6407 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 313.15 | 2 | 82834.6374 | 393124.8118 | 475959.4492 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 313.15 | 3 | 121302.5797 | 589687.2177 | 710989.7974 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.043699 | 313.15 | 4 | 171976.0617 | 786249.6236 | 958225.6853 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 285.9278 | 1 | 35986.1993 | 212549.7281 | 248535.9274 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 285.9278 | 2 | 52691.9925 | 425099.4562 | 477791.4487 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 285.9278 | 3 | 77161.8592 | 637649.1843 | 714811.0434 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 285.9278 | 4 | 109395.7993 | 850198.9123 | 959594.7116 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 295.0019 | 1 | 42936.225 | 215260.203 | 258196.428 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 295.0019 | 2 | 62868.4131 | 430520.4061 | 493388.8192 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 295.0019 | 3 | 92064.1526 | 645780.6091 | 737844.7617 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 295.0019 | 4 | 130523.4434 | 861040.8122 | 991564.2555 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 304.0759 | 1 | 49966.3702 | 210575.6933 | 260542.0636 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 304.0759 | 2 | 73162.147 | 421151.3867 | 494313.5337 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 304.0759 | 3 | 107138.2389 | 631727.08 | 738865.3189 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 304.0759 | 4 | 151894.6459 | 842302.7734 | 994197.4193 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 313.15 | 1 | 56129.7812 | 198496.199 | 254625.9802 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 313.15 | 2 | 82186.7845 | 396992.398 | 479179.1825 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 313.15 | 3 | 120353.8676 | 595488.597 | 715842.4646 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.043699 | 313.15 | 4 | 170631.0304 | 793984.796 | 964615.8264 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.033905 | 277.0389 | 15000
0.033905 | 280.9278 | 15000
0.033905 | 284.8167 | 15000
0.033905 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.043699 | 285.9278 | 15000
0.043699 | 295.0019 | 15000
0.043699 | 304.0759 | 15000
0.043699 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser