## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'F': 300.0-600.0 ton, 5.77 COP, 6.76 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 400078ce-11fe-4169-b06d-3cb4fb6dc619 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'F' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.067809 | 277.0389 | 0.086352 | 285.9278 | 1 | 69176.8429 | 389171.2044 | 458348.0473 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 285.9278 | 2 | 101308.4847 | 778342.4087 | 879650.8934 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 285.9278 | 3 | 147281.6553 | 1167513.6131 | 1314795.2684 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 285.9278 | 4 | 207096.3546 | 1556684.8175 | 1763781.1721 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 295.0019 | 1 | 83063.1315 | 386210.0193 | 469273.1508 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 295.0019 | 2 | 121644.7532 | 772420.0386 | 894064.7918 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 295.0019 | 3 | 176846.398 | 1158630.0579 | 1335476.4558 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 295.0019 | 4 | 248668.0658 | 1544840.0771 | 1793508.1429 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 304.0759 | 1 | 93601.6163 | 370413.4864 | 464015.1027 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 304.0759 | 2 | 137078.2116 | 740826.9728 | 877905.1844 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 304.0759 | 3 | 199283.4654 | 1111240.4592 | 1310523.9246 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 304.0759 | 4 | 280217.3777 | 1481653.9456 | 1761871.3233 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 313.15 | 1 | 99329.1813 | 341781.6057 | 441110.787 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 313.15 | 2 | 145466.1476 | 683563.2114 | 829029.359 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 313.15 | 3 | 211477.7955 | 1025344.8171 | 1236822.6126 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086352 | 313.15 | 4 | 297364.1248 | 1367126.4228 | 1664490.5476 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 285.9278 | 1 | 66698.0456 | 410923.9191 | 477621.9648 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 285.9278 | 2 | 97678.3219 | 821847.8383 | 919526.1602 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 285.9278 | 3 | 142004.1469 | 1232771.7574 | 1374775.9043 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 285.9278 | 4 | 199675.5203 | 1643695.6765 | 1843371.1969 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 295.0019 | 1 | 81074.552 | 411704.4381 | 492778.9901 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 295.0019 | 2 | 118732.5073 | 823408.8761 | 942141.3835 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 295.0019 | 3 | 172612.5928 | 1235113.3142 | 1407725.9069 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 295.0019 | 4 | 242714.8083 | 1646817.7522 | 1889532.5605 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 304.0759 | 1 | 92654.8716 | 399649.6092 | 492304.4808 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 304.0759 | 2 | 135691.7178 | 799299.2183 | 934990.9361 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 304.0759 | 3 | 197267.7891 | 1198948.8275 | 1396216.6166 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 304.0759 | 4 | 277383.0857 | 1598598.4367 | 1875981.5224 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 313.15 | 1 | 100083.5175 | 374759.4325 | 474842.9499 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 313.15 | 2 | 146570.862 | 749518.865 | 896089.7269 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 313.15 | 3 | 213083.8225 | 1124278.2974 | 1337362.1199 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086352 | 313.15 | 4 | 299622.3988 | 1499037.7299 | 1798660.1287 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 285.9278 | 1 | 65643.4248 | 419094.009 | 484737.4339 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 285.9278 | 2 | 96133.8451 | 838188.0181 | 934321.8631 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 285.9278 | 3 | 139758.7958 | 1257282.0271 | 1397040.8229 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 285.9278 | 4 | 196518.2771 | 1676376.0361 | 1872894.3132 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 295.0019 | 1 | 79867.3786 | 423616.232 | 503483.6106 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 295.0019 | 2 | 116964.6194 | 847232.4639 | 964197.0833 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 295.0019 | 3 | 170042.4481 | 1270848.6959 | 1440891.144 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 295.0019 | 4 | 239100.8648 | 1694464.9278 | 1933565.7926 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 304.0759 | 1 | 91676.8341 | 415303.1071 | 506979.9412 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 304.0759 | 2 | 134259.3959 | 830606.2142 | 964865.6101 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 304.0759 | 3 | 195185.4884 | 1245909.3212 | 1441094.8096 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 304.0759 | 4 | 274455.1115 | 1661212.4283 | 1935667.5398 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 313.15 | 1 | 99823.9332 | 394154.6344 | 493978.5676 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 313.15 | 2 | 146190.7046 | 788309.2688 | 934499.9734 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 313.15 | 3 | 212531.152 | 1182463.9031 | 1394995.0551 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086352 | 313.15 | 4 | 298845.2753 | 1576618.5375 | 1875463.8128 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 285.9278 | 1 | 66483.7052 | 413681.4741 | 480165.1793 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 285.9278 | 2 | 97364.4235 | 827362.9481 | 924727.3717 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 285.9278 | 3 | 141547.8033 | 1241044.4222 | 1382592.2255 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 285.9278 | 4 | 199033.8444 | 1654725.8963 | 1853759.7407 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 295.0019 | 1 | 80132.187 | 421945.401 | 502077.588 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 295.0019 | 2 | 117352.4275 | 843890.802 | 961243.2295 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 295.0019 | 3 | 170606.2412 | 1265836.203 | 1436442.4442 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 295.0019 | 4 | 239893.628 | 1687781.604 | 1927675.232 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 304.0759 | 1 | 91577.9303 | 417373.9801 | 508951.9105 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 304.0759 | 2 | 134114.5528 | 834747.9602 | 968862.5131 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 304.0759 | 3 | 194974.9164 | 1252121.9403 | 1447096.8567 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 304.0759 | 4 | 274159.021 | 1669495.9204 | 1943654.9415 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 313.15 | 1 | 99680.7062 | 399967.2114 | 499647.9176 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 313.15 | 2 | 145980.9508 | 799934.4228 | 945915.3736 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 313.15 | 3 | 212226.2131 | 1199901.6343 | 1412127.8474 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086352 | 313.15 | 4 | 298416.4932 | 1599868.8457 | 1898285.3389 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F2: Data group defining the lookup variables for cooling performance
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B2: Data group defining the lookup variables for standby performance
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.067809 | 277.0389 | 15000
0.067809 | 280.9278 | 15000
0.067809 | 284.8167 | 15000
0.067809 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.086352 | 285.9278 | 15000
0.086352 | 295.0019 | 15000
0.086352 | 304.0759 | 15000
0.086352 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on C3: Pressure difference across the condenser