## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'G': 600.0+ ton, 6.28 COP, 7.03 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | fdfd6663-12ab-4d4d-a8fb-569d2478a24a |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'G' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.92308 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.097947 | 277.0389 | 0.12322 | 285.9278 | 1 | 95861.0651 | 552588.9297 | 648449.9948 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 285.9278 | 2 | 136976.3706 | 1105177.8594 | 1242154.23 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 285.9278 | 3 | 193806.0149 | 1657766.7891 | 1851572.804 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 285.9278 | 4 | 266349.9981 | 2210355.7188 | 2476705.7169 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 295.0019 | 1 | 120203.5711 | 558114.4216 | 678317.9926 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 295.0019 | 2 | 171759.503 | 1116228.8431 | 1287988.3461 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 295.0019 | 3 | 243020.1988 | 1674343.2647 | 1917363.4635 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 295.0019 | 4 | 333985.6584 | 2232457.6863 | 2566443.3447 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 304.0759 | 1 | 134839.5274 | 538888.6139 | 673728.1412 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 304.0759 | 2 | 192672.8965 | 1077777.2277 | 1270450.1242 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 304.0759 | 3 | 272610.2765 | 1616665.8416 | 1889276.1181 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 304.0759 | 4 | 374651.6674 | 2155554.4554 | 2530206.1228 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 313.15 | 1 | 137588.5777 | 494911.5066 | 632500.0843 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 313.15 | 2 | 196601.0287 | 989823.0131 | 1186424.0418 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 313.15 | 3 | 278168.1377 | 1484734.5197 | 1762902.6574 | 0 | 0 | NORMAL
0.097947 | 277.0389 | 0.12322 | 313.15 | 4 | 382289.9046 | 1979646.0263 | 2361935.9308 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 285.9278 | 1 | 90401.1478 | 574936.9587 | 665338.1066 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 285.9278 | 2 | 129174.6666 | 1149873.9175 | 1279048.5841 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 285.9278 | 3 | 182767.4895 | 1724810.8762 | 1907578.3657 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 285.9278 | 4 | 251179.6164 | 2299747.8349 | 2550927.4514 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 295.0019 | 1 | 115611.4975 | 588065.3077 | 703676.8052 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 295.0019 | 2 | 165197.8654 | 1176130.6154 | 1341328.4807 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 295.0019 | 3 | 233736.2264 | 1764195.9231 | 1997932.1495 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 295.0019 | 4 | 321226.5805 | 2352261.2308 | 2673487.8113 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 304.0759 | 1 | 131948.416 | 576442.3571 | 708390.773 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 304.0759 | 2 | 188541.7725 | 1152884.7142 | 1341426.4866 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 304.0759 | 3 | 266765.205 | 1729327.0712 | 1996092.2762 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 304.0759 | 4 | 366618.7134 | 2305769.4283 | 2672388.1418 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 313.15 | 1 | 137259.1256 | 540068.1069 | 677327.2325 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 313.15 | 2 | 196130.2729 | 1080136.2138 | 1276266.4867 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 313.15 | 3 | 277502.0717 | 1620204.3207 | 1897706.3923 | 0 | 0 | NORMAL
0.097947 | 280.9278 | 0.12322 | 313.15 | 4 | 381374.5219 | 2160272.4275 | 2541646.9494 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 285.9278 | 1 | 87517.4292 | 580880.7936 | 668398.2228 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 285.9278 | 2 | 125054.1062 | 1161761.5873 | 1286815.6935 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 285.9278 | 3 | 176937.3643 | 1742642.3809 | 1919579.7452 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 285.9278 | 4 | 243167.2034 | 2323523.1745 | 2566690.3779 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 295.0019 | 1 | 112793.002 | 601611.9997 | 714405.0017 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 295.0019 | 2 | 161170.5026 | 1203223.9994 | 1364394.502 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 295.0019 | 3 | 228037.9653 | 1804835.9991 | 2032873.9644 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 295.0019 | 4 | 313395.39 | 2406447.9988 | 2719843.3888 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 304.0759 | 1 | 129827.5385 | 597591.9062 | 727419.4447 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 304.0759 | 2 | 185511.2398 | 1195183.8124 | 1380695.0521 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 304.0759 | 3 | 262477.3452 | 1792775.7185 | 2055253.0637 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 304.0759 | 4 | 360725.8549 | 2390367.6247 | 2751093.4796 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 313.15 | 1 | 136495.8398 | 568820.5131 | 705316.3528 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 313.15 | 2 | 195039.6098 | 1137641.0262 | 1332680.636 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 313.15 | 3 | 275958.9072 | 1706461.5392 | 1982420.4464 | 0 | 0 | NORMAL
0.097947 | 284.8167 | 0.12322 | 313.15 | 4 | 379253.7319 | 2275282.0523 | 2654535.7842 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 285.9278 | 1 | 87705.7639 | 570420.4344 | 658126.1983 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 285.9278 | 2 | 125323.2186 | 1140840.8688 | 1266164.0874 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 285.9278 | 3 | 177318.1277 | 1711261.3032 | 1888579.431 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 285.9278 | 4 | 243690.4913 | 2281681.7376 | 2525372.2289 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 295.0019 | 1 | 112589.337 | 598754.4976 | 711343.8346 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 295.0019 | 2 | 160879.4846 | 1197508.9951 | 1358388.4798 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 295.0019 | 3 | 227626.2079 | 1796263.4927 | 2023889.7006 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 295.0019 | 4 | 312829.5067 | 2395017.9903 | 2707847.497 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 304.0759 | 1 | 129663.5451 | 602337.2611 | 732000.8062 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 304.0759 | 2 | 185276.9087 | 1204674.5223 | 1389951.431 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 304.0759 | 3 | 262145.7933 | 1807011.7834 | 2069157.5768 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 304.0759 | 4 | 360270.199 | 2409349.0446 | 2769619.2436 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 313.15 | 1 | 136830.7678 | 581168.7251 | 717999.4929 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 313.15 | 2 | 195518.1902 | 1162337.4503 | 1357855.6405 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 313.15 | 3 | 276636.0441 | 1743506.1754 | 2020142.2195 | 0 | 0 | NORMAL
0.097947 | 288.7056 | 0.12322 | 313.15 | 4 | 380184.3295 | 2324674.9006 | 2704859.23 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.097947 | 277.0389 | 15000
0.097947 | 280.9278 | 15000
0.097947 | 284.8167 | 15000
0.097947 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.12322 | 285.9278 | 15000
0.12322 | 295.0019 | 15000
0.12322 | 304.0759 | 15000
0.12322 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser