## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'H': 0.0-300.0 ton, 5.77 COP, 6.39 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 708e4d54-6abe-460f-8341-31c7a93cf519 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'H' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.022603 | 277.0389 | 0.028784 | 285.9278 | 1 | 25102.7264 | 131279.4784 | 156382.2047 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 285.9278 | 2 | 34476.1207 | 262558.9567 | 297035.0774 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 285.9278 | 3 | 49243.5952 | 393838.4351 | 443082.0303 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 285.9278 | 4 | 69405.1498 | 525117.9134 | 594523.0633 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 295.0019 | 1 | 30419.4353 | 126694.5391 | 157113.9744 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 295.0019 | 2 | 41778.0964 | 253389.0782 | 295167.1747 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 295.0019 | 3 | 59673.2935 | 380083.6174 | 439756.9109 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 295.0019 | 4 | 84105.0264 | 506778.1565 | 590883.1829 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 304.0759 | 1 | 30523.4274 | 115116.3985 | 145639.8259 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 304.0759 | 2 | 41920.9193 | 230232.7971 | 272153.7164 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 304.0759 | 3 | 59877.293 | 345349.1956 | 405226.4886 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 304.0759 | 4 | 84392.5484 | 460465.5941 | 544858.1426 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 313.15 | 1 | 25716.9289 | 96545.0566 | 122261.9855 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 313.15 | 2 | 35319.6674 | 193090.1132 | 228409.7806 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 313.15 | 3 | 50448.4661 | 289635.1698 | 340083.6359 | 0 | 0 | NORMAL
0.022603 | 277.0389 | 0.028784 | 313.15 | 4 | 71103.3248 | 386180.2264 | 457283.5513 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 285.9278 | 1 | 24413.698 | 143355.2211 | 167768.9191 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 285.9278 | 2 | 33529.8081 | 286710.4423 | 320240.2504 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 285.9278 | 3 | 47891.9398 | 430065.6634 | 477957.6032 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 285.9278 | 4 | 67500.093 | 573420.8845 | 640920.9775 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 295.0019 | 1 | 31623.5267 | 142521.2936 | 174144.8204 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 295.0019 | 2 | 43431.7974 | 285042.5872 | 328474.3846 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 295.0019 | 3 | 62035.3394 | 427563.8808 | 489599.2203 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 295.0019 | 4 | 87434.1528 | 570085.1744 | 657519.3273 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 304.0759 | 1 | 33624.7798 | 134694.1648 | 168318.9446 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 304.0759 | 2 | 46180.3213 | 269388.3295 | 315568.6508 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 304.0759 | 3 | 65961.1639 | 404082.4943 | 470043.6582 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 304.0759 | 4 | 92967.3076 | 538776.659 | 631743.9666 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 313.15 | 1 | 30394.86 | 119873.8345 | 150268.6945 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 313.15 | 2 | 41744.3447 | 239747.6691 | 281492.0138 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 313.15 | 3 | 59625.0845 | 359621.5036 | 419246.5882 | 0 | 0 | NORMAL
0.022603 | 280.9278 | 0.028784 | 313.15 | 4 | 84037.0795 | 479495.3382 | 563532.4177 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 285.9278 | 1 | 22734.4699 | 146786.7501 | 169521.22 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 285.9278 | 2 | 31223.5539 | 293573.5001 | 324797.054 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 285.9278 | 3 | 44597.8264 | 440360.2502 | 484958.0766 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 285.9278 | 4 | 62857.2876 | 587147.0002 | 650004.2878 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 295.0019 | 1 | 31312.7545 | 149703.8343 | 181016.5887 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 295.0019 | 2 | 43004.9823 | 299407.6685 | 342412.6509 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 295.0019 | 3 | 61425.7027 | 449111.5028 | 510537.2055 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 295.0019 | 4 | 86574.9156 | 598815.3371 | 685390.2527 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 304.0759 | 1 | 34894.711 | 145627.7171 | 180522.4282 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 304.0759 | 2 | 47924.4466 | 291255.4343 | 339179.8809 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 304.0759 | 3 | 68452.3665 | 436883.1514 | 505335.5179 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 304.0759 | 4 | 96478.4706 | 582510.8685 | 678989.3392 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 313.15 | 1 | 33132.9187 | 134558.3987 | 167691.3173 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 313.15 | 2 | 45504.7985 | 269116.7973 | 314621.5958 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 313.15 | 3 | 64996.2881 | 403675.196 | 468671.4841 | 0 | 0 | NORMAL
0.022603 | 284.8167 | 0.028784 | 313.15 | 4 | 91607.3877 | 538233.5946 | 629840.9823 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 285.9278 | 1 | 20521.4984 | 141574.0652 | 162095.5635 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 285.9278 | 2 | 28184.2556 | 283148.1303 | 311332.3859 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 285.9278 | 3 | 40256.6775 | 424722.1955 | 464978.873 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 285.9278 | 4 | 56738.7641 | 566296.2607 | 623035.0248 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 295.0019 | 1 | 29935.3774 | 148242.1611 | 178177.5385 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 295.0019 | 2 | 41113.2907 | 296484.3222 | 337597.6129 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 295.0019 | 3 | 58723.7253 | 444726.4833 | 503450.2086 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 295.0019 | 4 | 82766.6814 | 592968.6444 | 675735.3258 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 304.0759 | 1 | 34773.2827 | 147917.0557 | 182690.3383 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 304.0759 | 2 | 47757.6767 | 295834.1114 | 343591.7881 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 304.0759 | 3 | 68214.1625 | 443751.1671 | 511965.3296 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 304.0759 | 4 | 96142.74 | 591668.2227 | 687810.9627 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 313.15 | 1 | 34362.9696 | 140598.7489 | 174961.7185 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 313.15 | 2 | 47194.1522 | 281197.4979 | 328391.65 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 313.15 | 3 | 67409.2583 | 421796.2468 | 489205.5051 | 0 | 0 | NORMAL
0.022603 | 288.7056 | 0.028784 | 313.15 | 4 | 95008.2879 | 562394.9957 | 657403.2836 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.022603 | 277.0389 | 15000
0.022603 | 280.9278 | 15000
0.022603 | 284.8167 | 15000
0.022603 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.028784 | 285.9278 | 15000
0.028784 | 295.0019 | 15000
0.028784 | 304.0759 | 15000
0.028784 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser