## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'T': 300.0-400.0 ton, 5.91 COP, 9.02 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 2df0827b-342c-42ef-8ef9-9ad8e47dae8f |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'T' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.85714 | -
| maximum | 1.1429 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.052741 | 277.0389 | 0.066919 | 285.9278 | 1 | 29900.0151 | 327352.5122 | 357252.5273 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 285.9278 | 2 | 62065.4582 | 654705.0244 | 716770.4827 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 285.9278 | 3 | 111163.5404 | 982057.5367 | 1093221.0771 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 285.9278 | 4 | 177194.2615 | 1309410.0489 | 1486604.3104 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 295.0019 | 1 | 33601.3422 | 304247.0246 | 337848.3668 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 295.0019 | 2 | 69748.5502 | 608494.0492 | 678242.5994 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 295.0019 | 3 | 124924.4909 | 912741.0739 | 1037665.5648 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 295.0019 | 4 | 199129.1644 | 1216988.0985 | 1416117.2629 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 304.0759 | 1 | 33239.8742 | 273388.2051 | 306628.0793 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 304.0759 | 2 | 68998.2268 | 546776.4102 | 615774.637 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 304.0759 | 3 | 123580.6097 | 820164.6153 | 943745.225 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 304.0759 | 4 | 196987.023 | 1093552.8204 | 1290539.8433 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 313.15 | 1 | 29293.1459 | 234776.0536 | 264069.1995 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 313.15 | 2 | 60805.7393 | 469552.1073 | 530357.8466 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 313.15 | 3 | 108907.2964 | 704328.1609 | 813235.4574 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066919 | 313.15 | 4 | 173597.8173 | 939104.2146 | 1112702.0318 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 285.9278 | 1 | 29228.9184 | 352654.4891 | 381883.4076 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 285.9278 | 2 | 60672.4181 | 705308.9782 | 765981.3963 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 285.9278 | 3 | 108668.5089 | 1057963.4673 | 1166631.9762 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 285.9278 | 4 | 173217.1908 | 1410617.9564 | 1583835.1473 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 295.0019 | 1 | 34375.0728 | 336422.7538 | 370797.8266 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 295.0019 | 2 | 71354.6344 | 672845.5075 | 744200.1419 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 295.0019 | 3 | 127801.0992 | 1009268.2613 | 1137069.3605 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 295.0019 | 4 | 203714.4671 | 1345691.015 | 1549405.4822 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 304.0759 | 1 | 35466.5563 | 312437.6865 | 347904.2427 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 304.0759 | 2 | 73620.2995 | 624875.373 | 698495.6725 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 304.0759 | 3 | 131859.0625 | 937313.0595 | 1069172.122 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 304.0759 | 4 | 210182.8453 | 1249750.7459 | 1459933.5912 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 313.15 | 1 | 32812.2946 | 280699.2873 | 313511.5818 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 313.15 | 2 | 68110.6712 | 561398.5746 | 629509.2458 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 313.15 | 3 | 121990.9361 | 842097.8619 | 964088.798 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066919 | 313.15 | 4 | 194453.0893 | 1122797.1491 | 1317250.2384 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 285.9278 | 1 | 27975.673 | 361742.4153 | 389718.0884 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 285.9278 | 2 | 58070.9729 | 723484.8306 | 781555.8036 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 285.9278 | 3 | 104009.1401 | 1085227.2459 | 1189236.3861 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 285.9278 | 4 | 165790.1747 | 1446969.6612 | 1612759.836 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 295.0019 | 1 | 34119.6288 | 352384.4322 | 386504.0611 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 295.0019 | 2 | 70824.3923 | 704768.8644 | 775593.2568 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 295.0019 | 3 | 126851.3988 | 1057153.2967 | 1184004.6955 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 295.0019 | 4 | 202200.6484 | 1409537.7289 | 1611738.3772 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 304.0759 | 1 | 36328.8342 | 335273.1172 | 371601.9514 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 304.0759 | 2 | 75410.1875 | 670546.2344 | 745956.4219 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 304.0759 | 3 | 135064.876 | 1005819.3516 | 1140884.2276 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 304.0759 | 4 | 215292.8998 | 1341092.4688 | 1556385.3686 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 313.15 | 1 | 34743.6057 | 310408.4703 | 345152.076 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 313.15 | 2 | 72119.6228 | 620816.9405 | 692936.5633 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 313.15 | 3 | 129171.2465 | 931225.4108 | 1060396.6572 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066919 | 313.15 | 4 | 205898.4767 | 1241633.881 | 1447532.3577 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 285.9278 | 1 | 26489.4089 | 354616.2908 | 381105.6997 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 285.9278 | 2 | 54985.8352 | 709232.5817 | 764218.4168 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 285.9278 | 3 | 98483.4444 | 1063848.8725 | 1162332.3169 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 285.9278 | 4 | 156982.2367 | 1418465.1634 | 1575447.4 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 295.0019 | 1 | 33234.7271 | 352132.06 | 385366.7871 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 295.0019 | 2 | 68987.5426 | 704264.12 | 773251.6626 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 295.0019 | 3 | 123561.4735 | 1056396.18 | 1179957.6535 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 295.0019 | 4 | 196956.5199 | 1408528.24 | 1605484.7599 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 304.0759 | 1 | 36277.0115 | 341894.4972 | 378171.5087 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 304.0759 | 2 | 75302.6155 | 683788.9945 | 759091.61 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 304.0759 | 3 | 134872.2072 | 1025683.4917 | 1160555.6989 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 304.0759 | 4 | 214985.7865 | 1367577.9889 | 1582563.7754 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 313.15 | 1 | 35587.9695 | 323903.6025 | 359491.5721 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 313.15 | 2 | 73872.3251 | 647807.2051 | 721679.5302 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 313.15 | 3 | 132310.4579 | 971710.8076 | 1104021.2655 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066919 | 313.15 | 4 | 210902.3678 | 1295614.4102 | 1506516.778 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.052741 | 277.0389 | 15000
0.052741 | 280.9278 | 15000
0.052741 | 284.8167 | 15000
0.052741 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.066919 | 285.9278 | 15000
0.066919 | 295.0019 | 15000
0.066919 | 304.0759 | 15000
0.066919 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser