## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'X': 150.0-300.0 ton, 4.90 COP, 5.60 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | c8cec7c5-96a2-4677-b361-752ee196fda1 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'X' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.033905 | 277.0389 | 0.044304 | 285.9278 | 1 | 42060.9251 | 198476.1651 | 240537.0903 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 285.9278 | 2 | 60792.7386 | 396952.3303 | 457745.0688 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 285.9278 | 3 | 85317.9377 | 595428.4954 | 680746.4331 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 285.9278 | 4 | 115636.5224 | 793904.6606 | 909541.183 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 295.0019 | 1 | 49402.6576 | 190379.5777 | 239782.2354 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 295.0019 | 2 | 71404.1082 | 380759.1555 | 452163.2637 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 295.0019 | 3 | 100210.1797 | 571138.7332 | 671348.9129 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 295.0019 | 4 | 135820.872 | 761518.311 | 897339.183 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 304.0759 | 1 | 57217.1809 | 177038.0893 | 234255.2703 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 304.0759 | 2 | 82698.8258 | 354076.1787 | 436775.0045 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 304.0759 | 3 | 116061.4481 | 531114.268 | 647175.7161 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 304.0759 | 4 | 157305.0476 | 708152.3574 | 865457.4049 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 313.15 | 1 | 63857.0868 | 158451.6999 | 222308.7867 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 313.15 | 2 | 92295.8107 | 316903.3999 | 409199.2105 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 313.15 | 3 | 129530.0789 | 475355.0998 | 604885.1787 | 0 | 0 | NORMAL
0.033905 | 277.0389 | 0.044304 | 313.15 | 4 | 175559.8914 | 633806.7997 | 809366.6912 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 285.9278 | 1 | 44302.9573 | 220770.9027 | 265073.86 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 285.9278 | 2 | 64033.2587 | 441541.8054 | 505575.0641 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 285.9278 | 3 | 89865.7587 | 662312.7082 | 752178.4669 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 285.9278 | 4 | 121800.4573 | 883083.6109 | 1004884.0682 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 295.0019 | 1 | 51853.5246 | 213498.0487 | 265351.5733 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 295.0019 | 2 | 74946.4677 | 426996.0973 | 501942.565 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 295.0019 | 3 | 105181.609 | 640494.146 | 745675.755 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 295.0019 | 4 | 142558.9486 | 853992.1947 | 996551.1433 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 304.0759 | 1 | 60534.729 | 200980.2936 | 261515.0226 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 304.0759 | 2 | 87493.8424 | 401960.5872 | 489454.4296 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 304.0759 | 3 | 122790.8854 | 602940.8808 | 725731.7662 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 304.0759 | 4 | 166425.8579 | 803921.1745 | 970347.0324 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 313.15 | 1 | 68823.5601 | 183217.6375 | 252041.1976 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 313.15 | 2 | 99474.1006 | 366435.2751 | 465909.3757 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 313.15 | 3 | 139604.2572 | 549652.9126 | 689257.1699 | 0 | 0 | NORMAL
0.033905 | 280.9278 | 0.044304 | 313.15 | 4 | 189214.0301 | 732870.5502 | 922084.5803 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 285.9278 | 1 | 46040.6205 | 231391.7632 | 277432.3837 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 285.9278 | 2 | 66544.7895 | 462783.5263 | 529328.3158 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 285.9278 | 3 | 93390.4992 | 694175.2895 | 787565.7886 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 285.9278 | 4 | 126577.7496 | 925567.0526 | 1052144.8022 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 295.0019 | 1 | 53041.5316 | 224942.6424 | 277984.174 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 295.0019 | 2 | 76663.553 | 449885.2849 | 526548.8379 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 295.0019 | 3 | 107591.4064 | 674827.9273 | 782419.3337 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 295.0019 | 4 | 145825.0916 | 899770.5698 | 1045595.6614 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 304.0759 | 1 | 61574.9833 | 213248.6207 | 274823.604 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 304.0759 | 2 | 88997.3735 | 426497.2415 | 515494.615 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 304.0759 | 3 | 124900.9757 | 639745.8622 | 764646.8379 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 304.0759 | 4 | 169285.79 | 852994.4829 | 1022280.273 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 313.15 | 1 | 70242.3631 | 196309.698 | 266552.0611 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 313.15 | 2 | 101524.7668 | 392619.396 | 494144.1629 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 313.15 | 3 | 142482.2098 | 588929.094 | 731411.3038 | 0 | 0 | NORMAL
0.033905 | 284.8167 | 0.044304 | 313.15 | 4 | 193114.6919 | 785238.792 | 978353.484 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 285.9278 | 1 | 47637.5961 | 230338.7464 | 277976.3426 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 285.9278 | 2 | 68852.9774 | 460677.4929 | 529530.4703 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 285.9278 | 3 | 96629.8636 | 691016.2393 | 787646.1029 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 285.9278 | 4 | 130968.2547 | 921354.9858 | 1052323.2405 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 295.0019 | 1 | 53542.1628 | 224713.3591 | 278255.5219 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 295.0019 | 2 | 77387.1401 | 449426.7182 | 526813.8582 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 295.0019 | 3 | 108606.9052 | 674140.0772 | 782746.9824 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 295.0019 | 4 | 147201.4582 | 898853.4363 | 1046054.8945 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 304.0759 | 1 | 61125.2309 | 213843.0707 | 274968.3016 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 304.0759 | 2 | 88347.324 | 427686.1414 | 516033.4655 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 304.0759 | 3 | 123988.6813 | 641529.2121 | 765517.8934 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 304.0759 | 4 | 168049.3026 | 855372.2828 | 1023421.5854 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 313.15 | 1 | 69112.5857 | 197727.8813 | 266840.4671 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 313.15 | 2 | 99891.8437 | 395455.7627 | 495347.6063 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 313.15 | 3 | 140190.5276 | 593183.644 | 733374.1715 | 0 | 0 | NORMAL
0.033905 | 288.7056 | 0.044304 | 313.15 | 4 | 190008.6374 | 790911.5253 | 980920.1628 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F2: Data group defining the lookup variables for cooling performance
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B2: Data group defining the lookup variables for standby performance
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.033905 | 277.0389 | 15000
0.033905 | 280.9278 | 15000
0.033905 | 284.8167 | 15000
0.033905 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.044304 | 285.9278 | 15000
0.044304 | 295.0019 | 15000
0.044304 | 304.0759 | 15000
0.044304 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on C3: Pressure difference across the condenser